## this week
aminpm | pminam |  |  |  | SUPERGROUP | ENGINEER_NAME | JOB_ID | SCHEDULE_DATE | DATE_OF_ACTION | TO_CHAR(WAL.DATE_OF_ACTION,'HH24:MI:SS') | APPOINTMENT_TYPE | DESCRIPTION | ENGINEER_COMMENTS | TIME_SLOT | COMPANY_NAME
0 | 1 | 0 | 0 | 0 | North East | Alex Dodds01 | 9208012 | 2021-05-10 | 2021-05-10 11:35 | 11:34:45 | 2 Way Appointment | Customer Installation fault | Cm10051109a , two undersized switch wires connected to meter landlord unable to confirm what they supply, advised by FTL to abort job and advise customer to get a electrician to find out what switch wires supply | P | Bespoke Metering
0 | 0 | 0 | 0 | 0 | North East | Thomas Flaherty | 8712495 | 2021-05-11 | 2021-05-11 13:14 | 13:13:34 | 2 Way Appointment | Customer Installation fault | Meter on landing cut out downstairs on VIR cable. Needs board on wall blocks and isolator. Tenant needs permission from landlord who is not available. Spoke to Chris Mason abort code cm11051312e | P | Bespoke Metering
0 | 0 | 0 | 0 | 0 | Scotland | Chris Lennie | 7064686 | 2021-05-12 | 2021-05-12 11:33 | 11:33:20 | 2 Way Appointment | Customer Installation fault | Comfort plus meter onsite | A | Bespoke Metering
0 | 1 | 0 | 0 | 0 | Scotland | Craig Paterson 01 | 8676309 | 2021-05-12 | 2021-05-12 09:33 | 09:32:54 | 2 Way Appointment | Customer REFUSES Install |  | P | Bespoke Metering
0 | 0 | 0 | 0 | 0 | North East | Jamie Sheen01 | 8730887 | 2021-05-13 | 2021-04-08 13:17 | 13:17:04 | 2 Way Appointment | Customer REFUSES Install Before instal Date |  | A | Bespoke Metering
0 | 0 | 0 | 0 | 0 | North East | Jamie Sheen01 | 8730887 | 2021-05-13 | 2021-04-08 13:17 | 13:17:04 | 2 Way Appointment | Customer REFUSES Install Before instal Date |  | A | Bespoke Metering
0 | 0 | 0 | 0 | 0 | Scotland | James McLean | 8676969 | 2021-05-12 | 2021-04-09 12:04 | 12:03:46 | 2 Way Appointment | Customer REFUSES Install Before instal Date |  | P | Bespoke Metering
0 | 0 | 0 | 0 | 0 | Scotland | Paul Simpson | 8694547 | 2021-05-13 | 2021-04-06 09:42 | 09:41:59 | 2 Way Appointment | Customer REFUSES Install Before instal Date |  | A | Bespoke Metering
0 | 0 | 0 | 0 | 0 | Scotland | Paul Simpson | 6725764 | 2021-05-12 | 2021-04-16 14:37 | 14:37:09 | 2 Way Appointment | Customer REFUSES Install Before instal Date |  | P | Bespoke Metering
1 | 0 | 0 | 0 | 0 | North East | Jamie Sheen01 | 8948809 | 2021-05-12 | 2021-05-12 13:28 | 13:28:12 | 2 Way Appointment | Duplicate Job | Job has been abort on the grounds it needs to raised a commercial credit. It is a single phase straight forward install that can be carried out by any bespoke engineer. Jamie | A | Bespoke Metering
1 | 0 | 0 | 0 | 0 | North East | Jamie Sheen01 | 8948809 | 2021-05-12 | 2021-05-12 13:28 | 13:28:12 | 2 Way Appointment | Duplicate Job | Job has been abort on the grounds it needs to raised a commercial credit. It is a single phase straight forward install that can be carried out by any bespoke engineer. Jamie | A | Bespoke Metering
0 | 0 | 0 | 0 | 0 | North East | Liam Flaherty01 | 9431689 | 2021-05-10 | 2021-05-10 15:58 | 15:58:19 | 2 Way Appointment | Duplicate Job | Spoken to RPS and smart mop regaling the fault and no one now why it¿¿¿s been sent out. Spoken to the customer and the said that a Engineer has attended at 12:30 and said there is nothing wrong with the gas meter but the main has been disconnected so the customer is speaking with NGN regarding this. | P | Bespoke Metering
0 | 0 | 0 | 0 | 0 | North East | Alex Breckman | 5083582 | 2021-05-12 | 2021-05-12 17:14 | 17:13:58 | 2 Way Appointment | No Access | Unable to locate correct fuse. Need to rebook and attend with.ftl and fuse finder | P | Bespoke Metering
0 | 0 | 0 | 0 | 0 | North East | Alex Breckman | 9469102 | 2021-05-12 | 2021-05-12 16:11 | 16:11:20 | 2 Way Appointment | No Access | No.access | P | Bespoke Metering
0 | 0 | 0 | 0 | 0 | North East | Alex Breckman | 2859417 | 2021-05-12 | 2021-05-12 11:07 | 11:07:01 | 2 Way Appointment | No Access | No answer at property no answer to phone | A | Bespoke Metering
0 | 0 | 0 | 0 | 0 | North East | Andrew Bulford | 2883851 | 2021-05-11 | 2021-05-11 16:17 | 16:17:05 | 2 Way Appointment | No Access | Called at property but no answer. Waited 10 minutes and tried again but no answer. Called customer but no answer, it just cut the call straight off. | P | Bespoke Metering
1 | 0 | 0 | 0 | 0 | North East | Andrew Bulford | 8713394 | 2021-05-12 | 2021-05-12 12:23 | 12:23:24 | 2 Way Appointment | No Access | Unable to gain access within a reasonable distance of the property. Over 800yards away is the nearest I can get parked. No access to the back of the property. Spoke to customer who is unable to make space as they don¿¿¿t own any of the cars outside. Spoke to S Snowdon about this issue. Not safe to walk that distance with tools, PPE etc. SS1205H | A | Bespoke Metering
0 | 0 | 0 | 0 | 0 | North East | Andrew Bulford | 2024441 | 2021-05-12 | 2021-05-12 08:55 | 08:54:56 | 2 Way Appointment | No Access | Unable to gain access to the building. Used intercom but no answer. Unable to gain access with trade button. Waited and called Customer but no luck. SS1205A | A | Bespoke Metering
0 | 0 | 0 | 0 | 0 | North East | Andrew Bulford | 8677281 | 2021-05-10 | 2021-05-10 13:26 | 13:25:54 | 2 Way Appointment | No Access | Called at property no answer. Spoke to neighbour who said he¿¿¿s not see anyone for a while. Waited 10 minutes and called customer but no answer. SS1005C | P | Bespoke Metering
0 | 0 | 0 | 0 | 0 | North East | Dale Burrell | 8731320 | 2021-05-12 | 2021-05-13 08:33 | 08:32:51 | 2 Way Appointment | No Access | Number on job not recognised. Tried to make contact numerous times throughout the day. Called in to NG who could not obtain any other contract details for the customer. Nobody on site | A | Bespoke Metering
0 | 0 | 0 | 0 | 0 | North East | Glen Robson 01 | 3901419 | 2021-05-11 | 2021-05-11 10:12 | 10:12:27 | 2 Way Appointment | No Access | No answer on intercom. Called contact number which is his mother. Advised he must call back in, also advised the concierge is required to open meter and fuse cupboards before we attend. | A | Bespoke Metering
1 | 0 | 0 | 0 | 0 | North East | Michael Ball01 | 8463314 | 2021-05-10 | 2021-05-10 14:00 | 13:59:30 | 2 Way Appointment | No Access | Agent has no keys for property | A | Bespoke Metering
0 | 0 | 0 | 0 | 0 | North East | Michael Ball01 | 8463312 | 2021-05-10 | 2021-05-10 14:16 | 14:15:41 | 2 Way Appointment | No Access | Incorrect keys for property, agent has been informed | P | Bespoke Metering
0 | 0 | 0 | 0 | 0 | North East | Michael Ball01 | 9300783 | 2021-05-12 | 2021-05-12 15:14 | 15:14:28 | 2 Way Appointment | No Access | Inconvenient, customer said he has to go to doctors to collect his medication...he said he was going to ring up and rearrange appointment CM12051458A | P | Bespoke Metering
0 | 0 | 0 | 0 | 0 | North East | Michael Charlton | 2858130 | 2021-05-10 | 2021-05-10 15:31 | 15:31:03 | 2 Way Appointment | No Access | Abort code SS1005D No access, tried mobile twice and went to 02 answer machine | P | Bespoke Metering
0 | 0 | 0 | 0 | 0 | North East | Michael Jennings | 9115336 | 2021-05-12 | 2021-05-12 15:13 | 15:12:47 | 2 Way Appointment | No Access | Green door. Key safe does not work used the number on notes to speak to them and give me other codes but did not work. | P | Bespoke Metering
0 | 0 | 0 | 0 | 0 | North East | Michael Jennings | 9115336 | 2021-05-12 | 2021-05-12 15:03 | 15:03:17 | 2 Way Appointment | No Access | Green door. Key safe does not work used the number on notes to speak to them and give me other codes but did not work. | P | Bespoke Metering
0 | 1 | 0 | 0 | 0 | North East | Rich Brannen | 8695342 | 2021-05-11 | 2021-05-11 11:19 | 11:19:10 | 2 Way Appointment | No Access | Void property getting re venerated no answer on phone number provided | P | Bespoke Metering
0 | 0 | 0 | 0 | 0 | North East | Stephen Paisley01 | 9431618 | 2021-05-10 | 2021-05-10 15:35 | 15:35:15 | 2 Way Appointment | No Access | Spoke to customer ,she is rebooking abort code ss1005e | P | Bespoke Metering
0 | 0 | 0 | 0 | 0 | North East | Stephen Paisley01 | 2935657 | 2021-05-11 | 2021-05-11 09:02 | 09:02:12 | 2 Way Appointment | No Access | Customer refused smet 1 install abort code cm111050853 | A | Bespoke Metering
0 | 0 | 0 | 0 | 0 | North East | Stephen Paisley01 | 9431618 | 2021-05-10 | 2021-05-10 15:36 | 15:36:30 | 2 Way Appointment | No Access | Spoke to customer ,she is rebooking abort code ss1005e | P | Bespoke Metering
0 | 0 | 0 | 0 | 0 | North East | Terry Cawley01 | 8677206 | 2021-05-10 | 2021-05-10 08:47 | 08:46:35 | 2 Way Appointment | No Access | Customer had to go help a family member at hospital will rebook | A | Bespoke Metering
0 | 1 | 0 | 0 | 0 | North East | Thomas Flaherty | 9245608 | 2021-05-12 | 2021-05-12 10:15 | 10:15:25 | 2 Way Appointment | No Access | Was void but new tenant on site. Spoke to Simon Abort code ss1205b | P | Bespoke Metering
0 | 1 | 0 | 0 | 0 | North East | Thomas Flaherty | 9245608 | 2021-05-12 | 2021-05-12 10:21 | 10:20:42 | 2 Way Appointment | No Access | Was void but new tenant on site. Spoke to Simon Abort code ss1205b | P | Bespoke Metering
0 | 0 | 0 | 0 | 0 | North East | Tim Boniface01 | 8498634 | 2021-05-12 | 2021-05-12 09:30 | 09:29:37 | 2 Way Appointment | No Access | Walk away, as there are dogs onsite | A | Bespoke Metering
0 | 1 | 0 | 0 | 0 | North East | Tim Boniface01 | 9096920 | 2021-05-11 | 2021-05-11 12:21 | 12:20:44 | 2 Way Appointment | No Access | Called customer no answer, left card , waited outside the property for 10 minutes | P | Bespoke Metering
1 | 0 | 0 | 0 | 0 | Scotland | Chris Lennie | 6546643 | 2021-05-11 | 2021-05-11 14:12 | 14:12:06 | 2 Way Appointment | No Access | No keys available for this void as someone has moved in | A | Bespoke Metering
0 | 0 | 0 | 0 | 0 | Scotland | Chris Lennie | 6472701 | 2021-05-12 | 2021-05-12 11:30 | 11:29:50 | 2 Way Appointment | No Access | No keys available, the property has been let. | A | Bespoke Metering
0 | 1 | 0 | 0 | 0 | Scotland | Chris Lennie | 9097475 | 2021-05-12 | 2021-05-12 11:31 | 11:31:11 | 2 Way Appointment | No Access | No keys available, the property has been let | P | Bespoke Metering
0 | 0 | 0 | 0 | 0 | Scotland | Chris Lennie | 8658416 | 2021-05-10 | 2021-05-10 13:14 | 13:14:03 | 2 Way Appointment | No Access | No answer pn phone, door entry system,;no answer | P | Bespoke Metering
0 | 1 | 0 | 0 | 0 | Scotland | Chris Stein | 7846709 | 2021-05-12 | 2021-05-12 09:27 | 09:27:17 | 2 Way Appointment | No Access | Door to flat was unlocked. Property is full of tennants stuff spoke to voids and they advised me to abort and they will speak to kingdom housing before we go in to change meter . | P | Bespoke Metering
1 | 0 | 0 | 0 | 0 | Scotland | Chris Stein | 4613654 | 2021-05-11 | 2021-05-11 12:42 | 12:41:42 | 2 Way Appointment | No Access | Spoke to dougie he wasn¿¿¿t aware house was all boarded up. | A | Bespoke Metering
0 | 0 | 0 | 0 | 0 | Scotland | Chris Stein | 8134339 | 2021-05-12 | 2021-05-12 10:18 | 10:18:19 | 2 Way Appointment | No Access | Went o rent locally to pick up keys. They gave me keys for property. When I got to property all houses looked tenanted so I phoned rent locally to see what house it was to be told they had emailed Lewis about this job as the tennant won¿¿¿t be out for another week. Spoke to voids | A | Bespoke Metering
0 | 0 | 0 | 0 | 0 | Scotland | Chris Stein | 8801978 | 2021-05-11 | 2021-05-11 09:17 | 09:17:11 | 2 Way Appointment | No Access | Locksmith cannot get access to property. Spoke to number on job to let them know we cannot do the job | A | Bespoke Metering
1 | 0 | 0 | 0 | 0 | Scotland | Gavin Brown | 9431287 | 2021-05-10 | 2021-05-10 12:39 | 12:39:23 | 2 Way Appointment | No Access | Keysafe number on the job does not work, tried clearing it and putting the number in multiple times. | A | Bespoke Metering
1 | 0 | 0 | 0 | 0 | Scotland | James McLean | 8498631 | 2021-05-10 | 2021-05-10 13:15 | 13:15:15 | 2 Way Appointment | No Access | Aborted by the warrant officer as there was a dog on site and there was no dog handler available. | A | Bespoke Metering
0 | 0 | 0 | 0 | 0 | Scotland | James McLean | 8498615 | 2021-05-10 | 2021-05-10 10:47 | 10:46:49 | 2 Way Appointment | No Access | Sttex for on site informed rp that we could not access property. | A | Bespoke Metering
0 | 0 | 0 | 0 | 0 | Scotland | John Coyle | 8587713 | 2021-05-10 | 2021-05-10 08:57 | 08:57:08 | 2 Way Appointment | No Access | Called en route 8.44 am no answer called again on site 8.51 am no answer No answer at door card left | A | Bespoke Metering
0 | 0 | 0 | 0 | 0 | Scotland | John Coyle | 9208638 | 2021-05-12 | 2021-05-12 14:18 | 14:17:33 | 2 Way Appointment | No Access | Semi con box customer has issues reading meter advised a Smets 2 install would resolve | P | Bespoke Metering
0 | 0 | 0 | 0 | 0 | Scotland | John Coyle | 4839874 | 2021-05-10 | 2021-05-10 10:12 | 10:12:11 | 2 Way Appointment | No Access | Called en route no answer called 3 times on site no answer customer let me in security entry but wouldn't open front door | A | Bespoke Metering
0 | 0 | 0 | 0 | 0 | Scotland | John Coyle | 8694383 | 2021-05-11 | 2021-05-11 15:11 | 15:10:32 | 2 Way Appointment | No Access | No answer at buzzer in privacy mode ,spoke to customer en route but not answering phone on arrival phone now switched off pics attached | P | Bespoke Metering
0 | 0 | 0 | 0 | 0 | Scotland | John Coyle | 8858104 | 2021-05-11 | 2021-05-11 09:39 | 09:38:38 | 2 Way Appointment | No Access | Cancelled spoke to Kieran | A | Bespoke Metering
0 | 0 | 0 | 0 | 0 | Scotland | John Coyle | 8837826 | 2021-05-11 | 2021-05-11 09:38 | 09:37:33 | 2 Way Appointment | No Access | Cancelled spoke to Kieran | A | Bespoke Metering
0 | 0 | 0 | 0 | 0 | Scotland | John Coyle | 2431894 | 2021-05-10 | 2021-05-10 09:45 | 09:45:25 | 2 Way Appointment | No Access | Called customer before arrival 9.30am he said there was someone in house on site no access customer called back and said his son was away out | A | Bespoke Metering
0 | 0 | 0 | 0 | 0 | Scotland | Jonny Thompson | 8409746 | 2021-05-10 | 2021-05-10 14:38 | 14:37:37 | 2 Way Appointment | No Access | No response from either number provided. Address is for council building. Asked around when at the council office but nobody able to provide any info. | P | Bespoke Metering
0 | 0 | 0 | 0 | 0 | Scotland | Jonny Thompson | 9096360 | 2021-05-10 | 2021-05-10 13:27 | 13:27:06 | 2 Way Appointment | No Access | No access information provided. No answer from door, key safe on wall. General code that council use doesn¿¿¿t work. Looks like property has tennants living there. | P | Bespoke Metering
0 | 0 | 0 | 0 | 0 | Scotland | Jonny Thompson | 9097470 | 2021-05-12 | 2021-05-12 15:36 | 15:35:56 | 2 Way Appointment | No Access | No access to stairwell. Trades buzzer not allowing access no answer from any flats. Key fob required | P | Bespoke Metering
0 | 0 | 0 | 0 | 0 | Scotland | Jonny Thompson | 8986415 | 2021-05-12 | 2021-05-12 15:19 | 15:18:55 | 2 Way Appointment | No Access | No access to stairwell. Trades buzzer not allowing access no answer from any flats. Key fob required | P | Bespoke Metering
1 | 0 | 0 | 0 | 0 | Scotland | Martin Gordon | 8676203 | 2021-05-11 | 2021-05-11 14:03 | 14:03:25 | 2 Way Appointment | No Access | Phoned customer to let him know that was on my way went to his Answering machine got to the customers flat chapped the door no answer tried phoning him again went to his Answering machine aborted no access went to next job | A | Bespoke Metering
0 | 0 | 0 | 0 | 0 | Scotland | Martin Gordon | 8658265 | 2021-05-10 | 2021-05-10 08:31 | 08:30:40 | 2 Way Appointment | No Access | Phoned customer no answer left word on there answering machine went to there door still no answer phoned them again no answer went to there answering machine left word again aborted job went to my next job | A | Bespoke Metering
0 | 0 | 0 | 0 | 0 | Scotland | Martin Gordon | 8985623 | 2021-05-12 | 2021-05-12 08:25 | 08:24:39 | 2 Way Appointment | No Access | Can¿¿¿t get into the street as it¿¿¿s all shut off due to new tram line getting done all one way and no access nitght mare to try and get to this place | A | Bespoke Metering
0 | 0 | 0 | 0 | 0 | Scotland | Martin Stephen | 9449408 | 2021-05-10 | 2021-05-10 15:08 | 15:08:11 | 2 Way Appointment | No Access | No answer card left | P | Bespoke Metering
0 | 0 | 0 | 0 | 0 | Scotland | Paul Simpson | 9226880 | 2021-05-12 | 2021-05-12 11:36 | 11:35:55 | 2 Way Appointment | No Access | No answer on Tennant's phone or property door.Arranged with Inverclyde centre rep for access. He turned up with keys however there is a dog present without the Tennant so didn't access the property. | A | Bespoke Metering
0 | 0 | 0 | 0 | 0 | Scotland | Paul Simpson | 9226878 | 2021-05-12 | 2021-05-12 11:04 | 11:03:39 | 2 Way Appointment | No Access | Phoned current Tennant no answer.Contacted Inverclyde centre for access but they don't have spare keys for entry to property. | A | Bespoke Metering
0 | 0 | 0 | 0 | 0 | Scotland | Paul Simpson | 2894145 | 2021-05-10 | 2021-05-10 14:30 | 14:29:57 | 2 Way Appointment | No Access | Arrived at lettings agency to be told the property now has a tenant. Receptionist phoned the tenant to see if it was suitable for today's appointment but doesn't suit. Tennant will contact Utilita for another booking. | P | Bespoke Metering
0 | 0 | 0 | 0 | 0 | Scotland | Robert Graham | 9097473 | 2021-05-12 | 2021-05-12 09:15 | 09:15:10 | 2 Way Appointment | No Access | Phoned three times no response. Left card. | A | Bespoke Metering
0 | 0 | 0 | 0 | 0 | Scotland | Robert Graham | 8658498 | 2021-05-12 | 2021-05-12 08:29 | 08:28:31 | 2 Way Appointment | No Access | Spoke to the customer on the phone not feeling well today would like to reschedule for another day. | A | Bespoke Metering
0 | 0 | 0 | 0 | 0 | Scotland | Robert Graham | 9376514 | 2021-05-11 | 2021-05-11 10:54 | 10:53:41 | 2 Way Appointment | No Access | Medium pressure gas supply. | A | Bespoke Metering
0 | 0 | 0 | 0 | 0 | Scotland | Thomas Leisk | 8694408 | 2021-05-10 | 2021-05-10 13:42 | 13:41:53 | 2 Way Appointment | No Access | No answer on both phones . Can hear house phone ringing at property. Left voicemail but nobody called back . No access | P | Bespoke Metering
1 | 0 | 0 | 0 | 0 | Scotland | William Fletcher01 | 8837856 | 2021-05-10 | 2021-05-10 15:53 | 15:52:54 | 2 Way Appointment | No Access | Job was cancelled by f2f. Spoke with Mercedes on the abort line | A | Bespoke Metering
0 | 0 | 0 | 0 | 0 | Scotland | William Fletcher01 | 8730911 | 2021-05-11 | 2021-05-11 11:15 | 11:15:11 | 2 Way Appointment | No Access | First number says ' number not recognised. Second number says ' cannot connect ' No one answering at the door or on the phone | A | Bespoke Metering
0 | 0 | 0 | 0 | 0 | Scotland | Thomas Leisk | 8676948 | 2021-05-12 | 2021-05-12 09:20 | 09:19:56 | 2 Way Appointment | No Mobile Signal | No signal at all at property or surrounding area. Had to drive about a mile just to on site job ! Customer is also shared with no8 . Customer wants smet2 meters as she had already told salesman about signal and cant vend etc if it fails. They said it would work !!! Call Customer for next install(smets2) and she can arrange access for neighbours as shared. | A | Bespoke Metering
0 | 0 | 0 | 0 | 0 | North East | Michael Ball01 | 8463307 | 2021-05-10 | 2021-05-10 13:14 | 13:13:34 | 2 Way Appointment | Notify DNO Damaged/missing phase barriers | Fused neutral in hinged metal cutout CM10051312B | P | Bespoke Metering
0 | 0 | 0 | 0 | 0 | North East | Stephen Paisley01 | 9357356 | 2021-05-10 | 2021-05-10 15:55 | 15:55:27 | 2 Way Appointment | Personal Safety Environment | Heavy rain and thunder 2 outside boxes | P | Bespoke Metering
0 | 0 | 0 | 0 | 0 | Scotland | Chris Lennie | 4520601 | 2021-05-10 | 2021-05-10 10:51 | 10:50:44 | 2 Way Appointment | Personal Safety Environment | This property is a shell, everywhere is damp there is mould everywhere and fungi growing on the door frame | A | Bespoke Metering
0 | 0 | 0 | 0 | 0 | Scotland | Jonny Thompson | 8499304 | 2021-05-10 | 2021-05-10 08:44 | 08:44:06 | 2 Way Appointment | Personal Safety Environment | Flat is disgusting. Needs cleaned. Neighbour thinks it¿¿¿s been broken into. Keysafe not working and door lying open. Council advised | A | Bespoke Metering
0 | 1 | 0 | 0 | 0 | North East | Glen Robson 01 | 8340880 | 2021-05-11 | 2021-05-11 12:38 | 12:38:11 | 2 Way Appointment | Refused Access | Customer does not want PP smart and wants to wait for SMETS 2 | P | Bespoke Metering
0 | 0 | 0 | 0 | 0 | Scotland | Martin Gordon | 8604786 | 2021-05-11 | 2021-05-04 14:00 | 13:59:52 | 2 Way Appointment | Refused Access | Client doesn't want meters installed today has e mailed utilita to try and cancel for today without success and says she couldn't phone as she has no credits left .Phoned scheduling team to contact her to reappointment. | P | Bespoke Metering
0 | 0 | 0 | 0 | 0 | Scotland | William Fletcher01 | 8837830 | 2021-05-10 | 2021-05-10 11:16 | 11:16:06 | 2 Way Appointment | Refused Access | Customer was refusing access and getting aggressive so the police were phoned . We were eventually given access and he settled the bill | A | Bespoke Metering
0 | 0 | 0 | 0 | 0 | Scotland | Thomas Leisk | 9245523 | 2021-05-11 | 2021-05-11 11:38 | 11:38:09 | 2 Way Appointment | Semi Concealed | Smets2 job. Not got brackets etc for semi concealed boxes . Offered customer leccy only but shes paying direct debit and would prefer both fuels to be done together. Spoke to barnesey and we will get stock ordered . Hopefully get this booked back in asap for customer | A | Bespoke Metering
0 | 0 | 0 | 0 | 0 | North East | Michael Charlton | 6412607 | 2021-05-11 | 2021-05-11 09:59 | 09:59:25 | 2 Way Appointment | Unable to access Isolation Point | Abort code CM11050958C Unable to gain access to fuse, bemco box padlocked, H key required. Gentoo also advised we require a permit to work in block of flats and Utilita need to contact them regarding this. | A | Bespoke Metering
0 | 0 | 0 | 0 | 0 | North East | Terry Cawley01 | 8463867 | 2021-05-12 | 2021-05-12 10:38 | 10:38:03 | 2 Way Appointment | Unable to access Isolation Point | Requires key access to main fuses also confined space for meter to fit into | A | Bespoke Metering
0 | 0 | 0 | 0 | 0 | Scotland | Alistair Cavan | 8658513 | 2021-05-11 | 2021-05-11 15:45 | 15:45:09 | 2 Way Appointment | Unable to access Isolation Point | No access to meter, boxed in remote fuse, customer will arrange access for next appointment. | P | Bespoke Metering
0 | 0 | 0 | 0 | 0 | Scotland | Chris Stein | 8986261 | 2021-05-11 | 2021-05-11 10:34 | 10:33:33 | 2 Way Appointment | Unable to access Isolation Point | Cannot locate fuse. Think it might be in number 5 but no answer at property. Spoke to voids | A | Bespoke Metering
0 | 0 | 0 | 0 | 0 | North East | Alex Breckman | 8727282 | 2021-05-11 | 2021-05-11 11:39 | 11:39:21 | 2 Way Appointment | Unable to Acheive Compliant Install | Boiler in attic with no ladder to carry out visual check. Customer will rebook and provide access. | A | Bespoke Metering
0 | 0 | 0 | 0 | 0 | North East | Andrew Bulford | 8712700 | 2021-05-12 | 2021-05-12 11:03 | 11:02:40 | 2 Way Appointment | Unable to Acheive Compliant Install | Undersized cables into L1 and N2. Unable to replace because of distance from cut out. SS1205C | A | Bespoke Metering
0 | 0 | 0 | 0 | 0 | North East | Rich Brannen | 8930179 | 2021-05-12 | 2021-05-12 16:42 | 16:41:44 | 2 Way Appointment | Unable to Acheive Compliant Install | SS1205Q Shelving is impeding the actual meter and will not come out or the kitchen unit for me to work safely . Customer needs the unit and shelving cleared so we can get in and up date the cables and instal a new iso and meter as it¿¿¿s also a shared multi phases fuse x3 and a single neutral. | P | Bespoke Metering
0 | 0 | 0 | 0 | 0 | North East | Tim Boniface01 | 8623058 | 2021-05-11 | 2021-05-11 14:43 | 14:42:45 | 2 Way Appointment | Unable to Acheive Compliant Install | Customer requires the electric meter to be lowered, as this is about 10ft high, and find it difficult to reach, please arange an install to be carryout so the meter can be lowered , a back board and a drill is required | P | Bespoke Metering
0 | 1 | 0 | 0 | 0 | Scotland | Chris Stein | 9115241 | 2021-05-11 | 2021-05-11 12:27 | 12:26:37 | 2 Way Appointment | Unable to Acheive Compliant Install | Cannot do install. Spoke to Scott in SmartMOP and advised to abort due to related mpans | P | Bespoke Metering
1 | 0 | 0 | 0 | 0 | Scotland | John Coyle | 8838108 | 2021-05-10 | 2021-05-10 13:40 | 13:39:56 | 2 Way Appointment | Unable to Acheive Compliant Install | Existing meter screwed to a metal panel nowhere suitable for smart meter | A | Bespoke Metering
1 | 0 | 0 | 0 | 0 | Scotland | Martin Gordon | 9134797 | 2021-05-12 | 2021-05-12 13:42 | 13:41:41 | 2 Way Appointment | Unable to Acheive Compliant Install | Couldn¿¿¿t do the gas as the customer is still with British Gas and not with UTILITA | A | Bespoke Metering
1 | 0 | 0 | 0 | 0 | Scotland | Martin Gordon | 9468604 | 2021-05-12 | 2021-05-12 16:37 | 16:37:16 | 2 Way Appointment | Unable to Acheive Compliant Install | No cover for gas meter old meter is water damaged told not to fit gas meter outside until they get a gas box to cover the new smart gas meter | A | Bespoke Metering
0 | 0 | 0 | 0 | 0 | Scotland | Paul Simpson | 9116000 | 2021-05-10 | 2021-05-10 09:41 | 09:41:28 | 2 Way Appointment | Unable to Acheive Compliant Install | Live & neutral tails from consumer unit are too short in length. Both have single insulation showing. These will need replaced in order to carry out a meter exchange. Shared fuse also with the property upstairs. This will need liasing with the homeowners upstairs to pull the fuse. | A | Bespoke Metering
1 | 0 | 0 | 0 | 0 | Scotland | William Fletcher01 | 8837854 | 2021-05-10 | 2021-05-10 15:02 | 15:02:02 | 2 Way Appointment | Unable to Acheive Compliant Install | Three phase head is feeding the three phase meter but also feeding 3 other meters. The other meters are feeding a trading company that works out the same building. So warrant officer has told me we can't change the meter today. Job is to be aborted. | A | Bespoke Metering
0 | 0 | 0 | 0 | 0 | North East | Glen Robson 01 | 8605289 | 2021-05-12 | 2021-05-12 11:36 | 11:35:41 | 2 Way Appointment | Unable to Locate | No contact details. Spoke to office, they tried Voids, no answer. Postcode is for a new housing estate!? | A | Bespoke Metering
0 | 0 | 0 | 0 | 0 | Scotland | William Fletcher01 | 8837844 | 2021-05-10 | 2021-05-10 11:44 | 11:44:21 | 2 Way Appointment | Unable to Locate | Meter serial on the warrant is different from the meter onsite. | A | Bespoke Metering
0 | 0 | 0 | 0 | 0 | North East | Terry Cawley01 | 9115215 | 2021-05-10 | 2021-05-10 15:36 | 15:36:05 | 2 Way Appointment | Vacant Property? | Unable to locate flat no 10 only goes to flat 8 no contact information on job notes | P | Bespoke Metering
1 | 0 | 0 | 0 | 0 | Scotland | Thomas Leisk | 8967149 | 2021-05-11 | 2021-05-11 16:40 | 16:39:32 | 2 Way Appointment | Vacant Property? | This was not a fault !! Void property. Spoke to Debbie at Inverclyde centre and she said that oak housing going to be ripping out storage heaters and will rebook when they need gas meter installed! | A | Bespoke Metering
0 | 0 | 0 | 0 | 0 | North East | Dale Burrell | 8587556 | 2021-05-11 | 2021-05-11 10:27 | 10:26:49 | 2 Way Appointment |  | Meter tails 1 & 2 unable to be changed due to running through walls from cut out which is at bottom of stairs. Meter is upstairs. Informed customer configuration would need to be upgraded to allow safe change of meter CM11050953B | A | Bespoke Metering
1 | 0 | 0 | 0 | 0 | North East | Glen Robson 01 | 9431390 | 2021-05-10 | 2021-05-10 12:45 | 12:45:08 | 2 Way Appointment |  | On supply fault, but 1 & 2 are VIR which disappear under floor to cutout which is approx 10 mtrs down the hall. Customer can top up as has key and card. DNO required to attend ASAP as requested by customer. SS1005B | A | Bespoke Metering
0 | 0 | 0 | 0 | 0 | North East | Michael Charlton | 4546783 | 2021-05-12 | 2021-05-12 10:59 | 10:58:36 | 2 Way Appointment |  | SS1205D Spoke to Simon regarding this job, advised report down as B code, snapped neutral screw and cut out needs updating | A | Bespoke Metering
1 | 0 | 0 | 0 | 0 | Scotland | Chris Lennie | 8675574 | 2021-05-11 | 2021-05-11 13:48 | 13:48:24 | 2 Way Appointment |  | There is a broken hole in the bottom of the cut out casing, customer wouldnt wait for a dno visit as she got work to go to, contacted the dno, they couldnt give me a reference number as a safety check visit couldnt be arrange today, no exposed conductors visible, calked customer to advise she call for a safety check, notes have been put on this address at the dno | A | Bespoke Metering
0 | 0 | 0 | 0 | 0 | Scotland | William Fletcher01 | 8837832 | 2021-05-10 | 2021-05-10 09:31 | 09:31:11 | 2 Way Appointment |  | Spoke with Craig Paterson about this job, the cutout has wing nut fuses which I am not allowed to touch so can't remove or change the meter. | A | Bespoke Metering
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0